## Slide 1: Design and analysis of Steel Connection Types
Prepared by: Dr. Rachel Chicchi , University of Cincinnati
with the support of the American Institute of Steel Construction
Introduction and Basic Principles
Version 1 – January 2022
Notes: This series of PowerPoint presentations covers the fundamentals of the design and analysis of steel connections. The intention of these slides was to focus on simple (shear) connections and include all aspects of connection design and detailing, including design procedures and constructability considerations. Given the volume of the content, basic fundamentals were provided which do not dig in closely to the design portion of the connections. If you would like slides related to specifics of shear connection design, you may reach out to Rachel Chicchi to obtain these additional slides.
The material can be used at the graduate or undergraduate level. Portions can also be used for construction management or architecture students.
The presentations are closely tied to the 2016 AISC Specification for Structural Steel Buildings (herein referred to as the AISC Specification). Despite the Specification containing both LRFD and ASD design formats, these PowerPoint presentations present only the LRFD format. The presentations discuss basic principles of the design and behavior of connections. The presentations are most effective if the students have a copy of the AISC Specification. A free copy can be downloaded from the AISC website, at: www.aisc.org. Access to the AISC Steel Construction Manual would also be ideal in order to access connection design tables. Information on student rates for physical and digital versions of the Steel Manual are also available at www.aisc.org.
For questions, comments, corrections, or suggestions on these presentations, please contact:
Rachel Chicchi
Civil & Architectural Engineering and Construction Management
University of Cincinnati
2850 Campus Way Drive
765 Baldwin Hall
Cincinnati, OH 45221
Email: rachel.chicchi@uc.edu
Acknowledgments:
These presentations were prepared with support from the AISC Teaching Aid Development Program. Overall coordination of this effort was provided by Kristi Sattler at AISC. The author gratefully acknowledges the support provided by AISC and the coordination and oversight provided by Dr. Sattler.
The author also gratefully acknowledges contributions and review provided by the AISC review committee for this project:
Hans Herrmann – Mississippi State University
Jason McCormick – University of Michigan
Tim Mrozowski – Michigan State University
Tom Schlafly - AISC

## Slide 2: Design and analysis of steel connections
1 - Introduction and Basic Principles
2 - Connection Basics: Bolts & Welds
3 - Constructability Considerations
Notes: This PowerPoint series is divided into 3 modules. This is the first module on: "Introduction and Basic Principles.“
Note that there were 3 other modules previously planned. Refer to the ReadMe for information on these modules and feel free to contact the author with requests for these additional files.

## Slide 3: 1- Introduction and Basic Principles
Definitions
Overview of AISC provisions for connections
Connection types
Limit states using tensile connection example
Additional limit states
Notes: These are the major topic areas to be covered in the first module.

## Slide 4: What are connections?
Steel connections are a combination of structural elements and joints used to transmit forces between two or more members.
Connections are critical for ensuring proper load path in a structural system.
Connections allow individual members (that can be easily fabricated, transported, and erected) to be connected to other members in order to create the structural frame.
Notes: This is the definition given in the AISC Specification.
Connections are typically used to promote ease of construction and erection. Individual members that can be fabricated, transported, and erected with ease are connected to other members in order to form the structural frame for the structure. Connections limit large member lengths and unusual member geometries.

## Slide 5: What are connections?
Primary method of connecting elements are:
Bolting
Welding
Notes: Bolts and welds are the primary methods for connecting structural steel elements. These two methods will be covered in more detail in Module 2.

## Slide 6: Load path
Transfer of load through members AND connections

## Slide 7: Load path
Continuous load paths must be provided to transfer all forces from the exposed region (often the floor) to the final point of resistance (the foundation).
To achieve this, connections are critical.

## Slide 8: Load path
Connections have their own load path as well.
For example:
- beam to the bolts
- bolts to the connection plate
- connection plate to welds
- welds to supporting beam
All must be adequately design to ensure structural integrity.

## Slide 9: Shop vs Field Connections
“Shop Connections” – connections made in the fabrication shop
- Welding preferably performed in the shop as opposed to the field due to controlled environment
- Members can be positioned for more economical welding (welding upside down is difficult)
- Welding may have an equipment advantage in the shop
- Shops use both welding and bolting
Notes: Welding can be performed using a variety of processes, as will be discussed in Module 2. These processes require different equipment, which is more or less portable than others. Thus, being able to weld in the shop allows the welder to use the best welding process for the specific application without needing to worry about the portability of the equipment in the field.

## Slide 10: Shop vs Field Connections
“Field Connections” – connections made in the field by the erector
- Bolting easily performed in the field and generally preferred when possible
- Bolting provides a method to erect the members and release the crane hook quickly

## Slide 11: Shop vs Field Connections
Quality welded and bolted connections can be achieved in both the shop and the field.
The choice between bolting and welding is complex and can depend on (among other factors):
      - geometry of the connection
      - properties of the connected members
      - available equipment
      - availability of qualified labor
  Connection designer must consider constructability. These decisions also play a large role in connection costs.

## Slide 12: Supporting vs supported member
When considering a beam connecting to a column or a beam to girder, the “supported member” is the beam which frames into the column or girder.
The beam transfers the load to the column or girder (called the “supporting member”) through the connection.

## Slide 13: Limit states
Limit State is a condition in which a structure or component becomes unfit for service and is judged either to have reached its ultimate load-carrying capacity (strength limit state) or to be no longer useful for its intended function (serviceability limit state).
Connections may have several limit states that must be considered for design.
The controlling strength limit state is the condition with the lowest resistance to the given design load.

## Slide 14: Limit states
Limit states can occur in:
- Fasteners (bolts or welds)
- Connecting elements (plates or tees)
- Supporting or supported members
Connections are typically proportioned based on strength requirements and then checked for serviceability (i.e. – ductility) as necessary.

## Slide 15: Limit states
Limit states will be presented using the Load and Resistance Factor Design (LRFD) approach per ANSI/AISC 360-16 Specification for Structural Steel Buildings (AISC 360-16).
Notes: Per the AISC 360-16 Preface:
The 2016 American Institute of Steel Construction’s Specification for Structural Steel Buildings provides an integrated treatment of allowable strength design (ASD) and load and resistance factor design (LRFD), and replaces earlier Specifications. As indicated in Chapter B of the Specification, designs can be made according to either ASD or LRFD provisions
ASD is certainly a permitted design method; however, focus will be given to LRFD design equations and LRFD load combinations because this is the more commonly used approach in industry today.

## Slide 16: Load and resistance factor Design (LRFD)
The required strength of the connections shall be determined by structural analysis for the specified design loads, consistent with the type of construction specified, or shall be a proportion of the required strength of the connected members when so specified herein. (Section J1.1, AISC 360-16)

## Slide 17: Connection Ductility
Connection ductility means that the connection is able to achieve the expected deformations without significant loss of strength.
These connection deformations can be achieved through:
- Connection flexural yielding
- Bearing deformations at bolt holes
- Rotations at the support
- Bolt or weld deformations
Notes: Connection ductility is critical to the adequate performance of steel connections.
From AISC 360-16 Commentary:
“The ductility required of a connection will depend upon the particular application. For example, the ductility requirement for a braced frame in a nonseismic area will generally be less than the ductility required in a high seismic area. The rotation ductility requirements for seismic design depend upon the structural system.”

## Slide 18: 1- Introduction and Basic Principles
Definitions
Overview of AISC provisions for connections
Connection types
Limit states using tensile connection example
Additional limit states

## Slide 19: AISC Design Provisions
Steel Construction Manual includes:
Design considerations and design tables in Parts 1 – 15
ANSI/AISC 360-16 – Specification for Structural Steel Buildings (Part 16.1)
Specification for Structural Joints Using High-Strength Bolts (Part 16.2)
Code of Standard Practice for Steel Buildings and Bridges (Part 16.3)
Notes: The Specification will refer to AISC 360-16. The Steel Manual will refer to the 15th Edition Steel Construction Manual, including all of the information provided on this slide.
AISC Design Examples are also available which illustrate the application of tables and specification provisions. This can be found at https://www.aisc.org/publications/steel-construction-manual-resources
The AISC teaching aid library contains a condensed version of the AISC Design Examples for use in a first semester steel design class. The condensed PDF can be accessed at: https://www.aisc.org/education/university-programs/ta-steel-construction-manual-design-examples-v15.1/

## Slide 20: Steel construction manual
Part 7 – Design Considerations for Bolts including:
General Requirements (bolts, washers, nuts) Eccentrically Loaded Bolt Groups Design Tables for: - available shear strength of bolts - available tensile strength of bolts - bearing/tearout strength
Part 8 – Design Considerations for Welds including:
General Requirements Concentrically Loaded Weld Groups Eccentrically Loaded Weld Groups Design Tables for eccentric weld groups

## Slide 21: Steel construction manual
Part 9 – Design of Connecting Elements including:
Whitmore Section Connecting Elements Subject to: - combined loading, tension, shear, block shear, coped beam strength, etc. Design Tables for: - section modulus for coped beam - block shear

## Slide 22: Steel construction manual
Part 10 – Design of Simple Shear Connections including:
Connection Alternatives/Constructability Double-Angle Connections & design tables Shear End-Plate Connections & design tables Unstiffened Seated Connections & design tables Stiffened Seated Connections & design tables Single-Plate Connections & design tables Single-Angle Connections & design tables Tee Connections & design tables

## Slide 23: Steel construction manual
Part 11 – Design of Partially Restrained Moment Connections
Part 12 – Design of Fully Restrained Moment Connections including:
FR Connections with wide-flange columns FR Moment splices FR Connections with HSS

## Slide 24: AISC Specification (aisc 360-16)
Chapter J – Design of Connections
J1. General Provisions
J2. Welds
J3. Bolts and Threaded Parts
J4. Affected Elements of Members and Connecting Elements
J5. Fillers
J6. Splices
J7. Bearing Strength
J8. Column Bases and Bearing on Concrete
J9. Anchor Rods and Embedments
J10. Flanges and Webs with Concentrated Forces

## Slide 25: AISC Specification (aisc 360-16)
Chapter K – Additional Requirements for HSS and Box-Section Connections
K1. General Provisions and Parameters for HSS Connections
K2. Concentrated Forces on HSS
K3. HSS-to-HSS Truss Connections
K4. HSS-to-HSS Moment Connections
K5. Welds of Plates and Branches to Rectangular HSS

## Slide 26: RCSC Specification
RCSC Specification for Structural Joints Using High-Strength Bolts –
Prepared by Research Council on Structural Connections (RCSC) with the participation of AISC
2014 version is in Part 16.2 of the AISC Steel Manual, 15th Edition
2020 RCSC is available for free download at: aisc.org/publications/steel- standards/
Notes: AISC Design Examples are also available which illustrate the application of tables and specification provisions. This can be found at www.aisc.org

## Slide 27: AISC Design Provisions
2020 RCSC Specification for Structural Joints Using High-Strength Bolts
Section 1 – General Requirements
Section 2 – Bolting Components and Assemblies
Section 3 – Bolted Parts
Section 4 – Joint Type
Section 5 – Limit States in Bolted Joints
Section 6 – Use of Washers
Section 7 – Pre-Installation Verification
Section 8 – Installation

## Slide 28: AISC Design Provisions
2020 RCSC Specification for Structural Joints Using High-Strength Bolts
Section 9 – Inspection
Section 10 – Arbitration
Appendix A – Testing Method to Determine the Slip Coefficient for Coatings Used in Bolted Joints

## Slide 29: 1- Introduction and Basic Principles
Definitions
Overview of AISC provisions for connections
Connection types
Limit states using tensile connection example
Additional limit states

## Slide 30: Connection types
Connections are classified by:
the type of force being transferred (i.e. – shear, moment, axial, etc.)
the specific components used in the connection (i.e. – bolted/welded, angle/plate, etc.)
the members being connected (i.e. - beam-to-column, beam-to-girder, etc.)
Notes: Specific connection types and their design procedures will be covered in the other modules. The following slides provide examples of different types of connections as categorized by force type per the AISC Specification.

## Slide 31: Connection types
Connection selection typically depends on:
Strength and stiffness required
Economy
Difficulty or ease of erection
Preferences of the fabricator/erector (usually due to economy or ease of erection)

## Slide 32: Tensile Connections
Direct Loaded Connection
Hanger Connection
Bracing Connections

## Slide 33: Compressive Connections
Column splices
Beam bearing plates
Column base plates

## Slide 34: Simple connections
Double-angle
Single-angle
Shear Tab
Shear End-Plate
Tee
Stiffened Seated
Unstiffened Seated
Notes: A simple connection transmits a negligible moment. In the analysis of the structure, simple connections may be assumed to allow unrestrained relative rotation between the framing elements being connected. A simple connection shall have sufficient rotation capacity to accommodate the required rotation determined by the analysis of the structure. (AISC 360-16)

## Slide 35: Moment connections
Flange Welded
Flange Plate Bolted
Tee-Stub
Flange Angle
Moment End-Plate
Notes: Two types of moment connections, fully restrained and partially restrained, are permitted, as specified below.
From AISC 360-16:
A fully restrained (FR) moment connection transfers moment with a negligible rotation between the connected members. In the analysis of the structure, the connection may be assumed to allow no relative rotation. An FR connection shall have sufficient strength and stiffness to maintain the initial angle between the connected members at the strength limit states.
Partially restrained (PR) moment connections transfer moments, but the rotation between connected members is not negligible. In the analysis of the structure, the force-deformation response characteristics of the connection shall be included. The response characteristics of a PR connection shall be documented in the technical literature or established by analytical or experimental means. The component elements of a PR connection shall have sufficient strength, stiffness and deformation capacity at the strength limit states.

## Slide 36
Fig. C-B3.3. Classification of moment-rotation response of fully restrained (FR), partially restrained (PR), and simple connections
Notes: From AISC 360-16 Commentary:
The strength of a connection is the maximum moment that it is capable of carrying, Mn. The strength of a connection can be determined on the basis of an ultimate limit-state model of the connection, or from physical tests. If the moment-rotation response does not exhibit a peak load then the strength can be taken as the moment at a rotation of 0.02 rad (Hsieh and Deierlein, 1991; Leon et al., 1996). It is also useful to define a lower limit on strength below which the connection may be treated as a simple connection. Connections that transmit less than 20% of the fully plastic moment of the beam at a rotation of 0.02 rad may be considered to have no flexural strength for design. However, it should be recognized that the aggregate strength of many weak connections can be important when compared to that of a few strong connections (FEMA, 1997).
In Figure C-B3.3, the points marked Mn indicate the maximum strength states of the example connections. The points marked θu indicate the maximum rotation states of the example connections. Note that it is possible for an FR connection to have a strength less than the strength of the beam. It is also possible for a PR connection to have a strength greater than the strength of the beam. The strength of the connection must be adequate to resist the moment demands implied by the design loads.

## Slide 37: 1- Introduction and Basic Principles
Definitions
Overview of AISC provisions for connections
Connection types
Limit states using tensile connection example
Additional limit states
Notes: In this next section, limit states and load paths will be explored using a tensile connection as an example.

## Slide 38: Limit states: Tension connection example
single angle bracing member
gusset plate
bolts
weld
Notes: This conceptual example helps to show the process of following load paths to identify limit states. Limit state equations will be shown but no math will be directly applied. The intention is to illustrate the different limit states and the thought-process of working through the load path to determine the demands and limit states.

## Slide 39: Limit states: Tension connection example
single angle bracing member
gusset plate
bolts
weld
Load Path
Angle  Bolts  Gusset plate  Weld  Support
Notes: A gusset plate is fixed to a support and bolted to a single angle. A load to the right is being applied to the angle.
The load path will be from the angle to the bolts, then to the gusset plate, then to the weld and then to the support. Demands and limit states for each of these components must be checked to determine the controlling limit state for the connection.

## Slide 40: Limit states: Tension connection example
Single Angle
1. Tensile Yielding
1
1
Notes: The angle is being pulled in tension so Section J4.1 (Strength of Elements in Tension) in AISC 360-16 would need to be considered. This section lists tensile yielding in the gross section and tensile rupture in the net section as potential failure modes.
Tensile yielding would occur across the gross section, as is shown in Section 1 on the slide (it does not occur at bolt hole locations).

## Slide 41: Limit states: Tension connection example
1. Tensile Yielding
Yielding of the angle in the gross section (at dashed line 1).
1
1

## Slide 42: Limit states: Tension connection example
Gross & Net Effective Area (B4.3)
Gross Area (B4.3a)
The gross area, Ag, of a member is the total cross-sectional area
Ag
bolt hole
Notes: The gross area is the full cross-sectional area of the member and does not consider bolt holes in the area calculation.

## Slide 43: Limit states: Tension connection example
Single Angle
1. Tensile Yielding
2. Tensile Rupture
2
2
1
1
Notes: Tensile rupture occurs across the net section, as indicated by Section 2. This is where the section crosses a bolt hole. Typically the section with the smallest net section would control the tensile rupture capacity; i.e. locations where there are more bolts and, thus, a smaller net section would produce lower tensile rupture strengths.

## Slide 44: Limit states: Tension connection example
2. Tensile Rupture
Tensile rupture in the net section (at dashed line 2)
2
2
Notes: Instead of using the gross area, an effective net area, Ae, is used.

## Slide 45: Tensile Rupture
2. Tensile Rupture
Notes: Results from experimental testing (photo courtesy of Jason McCormick at University of Michigan). Tension rupture occurs along the left-most line of bolts.

## Slide 46: Limit states: Tension connection example
2. Tensile Rupture
Effective Net Area, Ae (Section D3)
An, the net area, shall be determined in accordance with the provisions of Section B4.3
U, the shear lag factor, is determined as shown in Table D3.1

## Slide 47: Limit states: Tension connection example
Gross & Net Effective Area (B4.3)
Net Area (B4.3b)
The net area, An, of a member is the sum of the products of the thickness and the net width of each element
In computing net area for tension and shear, the width of a bolt hole shall be taken as 1/16 in. greater than the nominal dimension of the hole.
bolt hole
tleg
dhole
An

## Slide 48: Limit states: Tension connection example
Gross & Net Effective Area (B4.3)
Net Area (B4.3b)
Ag = gross area excluding hole
tleg = thickness of the angle leg
dhole = diameter of the bolt hole
An
bolt hole
Ag
tleg
dhole
Notes: From Steel Construction Manual: The width of the bolt hole is to be taken as 1/16” greater than the nominal dimension of the hole (per B4.3b). The additional 1/16” is added because of possible damage around the hole that may occur during drilling or punching operations.

## Slide 49: Limit states: Tension connection example
Shear Lag, U
Nonuniform tensile stress distribution in a member or connecting element in the vicinity of a connection.
The U factor accounts for the fact that the entire net section is not contributing to carrying stress.
Shear lag occurs when all elements of a member are not connected as part of the connection.
Notes: From AISC Design Guide 17:
The full cross-sectional area of the shape may have to be discounted (in addition to the fact that holes are present) in order to be able to predict the capacity of the member. This phenomenon is referred to as shear lag.
It occurs when all of the elements are not connected as part of the connection (for instance, if only one leg of an angle is connected to the other member).
The most obvious geometrical features that determines the severity of the shear lag are (a) the displacement of the centroids of the gusset plates relative to the member and (b) the length of the connection. Physical testing has shown that other features such as the ductility of the material being joined, the method of making the holes (e.g., punched or drilled), the proximity of one hole to another, and so on, generally have a small influence.
Although a number of investigations have been performed to study the shear lag effect, the current North American design standards are based mostly on the work of Munse and Chesson. This work included examination of different cross-sectional configurations, connections, materials, and fabrication methods. An empirical equation to calculate the net section efficiency was proposed. It was based on the test results of 218 specimens. This equation was verified further by a comparison with more than 1000 other test data.
Munse, W.H. and Chesson, E. Jr., "Riveted and Bolted Joints: Net Section Design," J. of the Struct.
Div., ASCE, Vol. 89 (1),. 107–126, 1963.
Chesson, E., Jr., and Munse, W.H., "Riveted and Bolted Joints: Truss Type Tensile Connections," J. of
the Struct. Div., ASCE, Vol. 89 (1), 67–106, 1963.

## Slide 50: Limit states: Tension connection example
Shear Lag, U
Notes: You can demonstrate shear lag using 2 sheets of paper – a flat piece to represent the gusset and a folded piece to represent the angle. Staple the pieces together. Have one student hold the gusset and have another hold both legs of the angle. Show that the paper in the angle isn’t taut in the “not stressed” portion shown above.

## Slide 51
(portion of table, AISC 360-16)

## Slide 52: Limit states: Tension connection example
Single Angle
1. Tensile Yielding
2. Tensile Rupture
3. Block Shear
2
1
1
3
3
Notes: The third possible limit state is block shear, as shown by Section 3 in the diagram.

## Slide 53: Limit states: Tension connection example
3. Block Shear (J4.3)
An area subjected to shear and tension, resulting in a “block” of material tearing out.
3
3
tension
shear
Notes: In a connection, block shear is a limit state of tension rupture along one path (in this case the blue line) and shear yielding or shear rupture (in this case the red line) along another path.

## Slide 54: Block shear
3. Block Shear (J4.3)
Must consider all potential block shear patterns and be evaluated to determine what controls.
Consider the gusset plate shown below.
gusset plate
Notes: There may be multiple possible block shear patterns that would need to be evaluated. Each possible pattern must be calculated and the controlling block shear pattern would need to be determined.

## Slide 55: Block Shear
3. Block Shear (J4.3)
One possible mode of block shear
shear
shear
tension

## Slide 56: Block Shear
3. Block Shear (J4.3)
Reference approval needed?
Notes: Results from experimental testing (R. Leon at Georgia Tech). Block shear failure in gusset plate: images with and without bolts.

## Slide 57: Block Shear
3. Block Shear (J4.3)
Another possible mode of block shear
shear
tension

## Slide 58: Limit states: Tension connection example
3. Block Shear (J4.3)
Block shear rupture along a shear path or paths and a perpendicular tension failure path:
shear
tension
Notes: Section J4.3 of the Commentary provides some additional discussion regarding block shear at coped beams:
Tests on coped beams indicated that a tearing failure mode (rupture) can occur along the perimeter of the bolt holes (Birkemoe and Gilmor, 1978). This block shear mode combines tensile failure on one plane and shear failure on a perpendicular plane. The failure path is defined by the centerlines of the bolt holes. This same condition exists on welded connections at beam copes. The tensile plane is the length of the horizontal portion of the weld and the shear plane runs from the horizontal weld to the bottom of the cope. The block shear failure mode is not limited to coped ends of beams; other examples are shown on the next slide. The block shear failure mode must also be checked around the periphery of welded connections.
This Specification has adopted a conservative model to predict block shear strength. The mode of failure in coped beam webs and angles is different than that of gusset plates because the shear resistance is present on only one plane, in which case there must be some rotation of the block of material that is providing the total resistance.

## Slide 59: Limit states: Tension connection example
  3. Block Shear (J4.3)
  Ubs = 1.0 where the tension stress is uniform
  Ubs = 0.5 where the tension stress is nonuniform
Notes: The block shear equation includes the term Ubs, a reduction coefficient.

## Slide 60: Limit states: Tension connection example
  3. Block Shear (J4.3)
where Ubs = 1.0
where Ubs = 0.5
Examples per J4.3 Commentary
Notes: Section J4.3 of the Commentary provides some additional discussion regarding block shear:
Although tensile failure is observed through the net section on the end plane, the distribution of tensile stresses is not always uniform (Ricles and Yura, 1983; Kulak and Grondin, 2001; Hardash and Bjorhovde, 1985). A reduction factor, Ubs, has been included in Equation J4-5 to approximate the nonuniform stress distribution on the tensile plane. The tensile stress distribution is nonuniform in the two row connection in Figure C-J4.2(b) because the rows of bolts nearest the beam end pick up most of the shear load. For conditions not shown in Figure C-J4.2, Ubs may be taken as (1 − e / l), where e / l is the ratio of the eccentricity of the load to the centroid of the resistance divided by the block length. This fits data reported by Kulak and Grondin (2001), Kulak and Grondin (2002), and Yura et al. (1982).
Block shear is a rupture or tearing phenomenon, not a yielding limit state. However, gross yielding on the shear plane can occur when tearing on the tensile plane commences if 0.6FuAnv exceeds 0.6FyAgv. Hence, Equation J4-5 limits the term 0.6FuAnv to not greater than 0.6FyAgv (Hardash and Bjorhovde, 1985). Equation J4-5 is consistent with the philosophy in Chapter D for tension members where the gross area is used for the limit state of yielding and the net area is used for the limit state of rupture.
Birkemoe, P.C. and Gilmor, M.I. (1978), “Behavior of Bearing-Critical Double-Angle Beam Connections,” Engineering Journal, AISC, Vol. 15, No. 4, pp. 109–115.
Hardash, S.G. and Bjorhovde, R. (1985), “New Design Criteria for Gusset Plates in Tension,” Engineering Journal, AISC, Vol. 22, No. 2, pp. 77–94.
Kulak, G.L. and Grondin, G.Y. (2001), “AISC LRFD Rules for Block Shear—A Review,” Engineering Journal, AISC, Vol. 38, No. 4, pp. 199–203
Ricles, J.M. and Yura, J.A. (1983), “Strength of Double-Row Bolted Web Connections,” Journal of the Structural Division, ASCE, Vol. 109, No. ST1, pp. 126–142
Yura, J.A., Birkemoe, P.C. and Ricles, J.M. (1982), “Beam Web Shear Connections: An Experimental Study,” Journal of the Structural Division, ASCE, Vol. 108, No. ST2, pp. 311–326.

## Slide 61: Limit states: Tension connection example
Single Angle
1. Tensile Yielding
2. Tensile Rupture
3. Block Shear
4. Bearing and Tearout at Bolt Holes
1
1
3
3
4
Notes: The next limit state is bearing and tearout at bolt holes.

## Slide 62: Limit states: Tension connection example
4. Bearing and Tearout at Bolt Holes (J3.10)
Bearing: deformation of material at the loaded edge of the bolt holes
Tearout: block shear rupture between bolts or at the edge due to bearing
Notes: If this bolt is close to the end of the connected part, then obviously one possible limit state is that a block of material will shear out between the bolt and the end of the connected part. The other possibility is that excessive deformations occur as the connected material yields. Often, a combination of these two features is observed in tests.
Reference: AISC Design Guide 17

## Slide 63: Limit states: Tension connection example
4. Bearing and Tearout at Bolt Holes (J3.10)
Tearout Fracture
Bearing Yield
Notes: From AISC 360-16 Commentary:
Bearing strength values are provided as a measure of the strength of the material upon which a bolt bears, not as a protection to the fastener, which needs no such protection. Accordingly, the same bearing value applies to all joints assembled by bolts, regardless of fastener shear strength or the presence or absence of threads in the bearing area. Material bearing strength may be limited either by bearing deformation of the hole or by tearout (a bolt-by-bolt block shear rupture) of the material upon which the bolt bears.

## Slide 64: Limit states: Tension connection example
4. Bearing and Tearout at Bolt Holes (J3.10)
When the clear distance, lc , is large enough (greater than 2d), bearing around the bolt holes may occur
lc
d = diameter of bolt

## Slide 65: Limit states: Tension connection example
4. Bearing and Tearout at Bolt Holes (J3.10)
Notes: In previous editions of the Specification, both limit states were defined by one equation and termed bearing limit states. In AISC 360-16, the limit states were separated to permit clear reference to each of the limits and their corresponding equations.
From AISC 360-16 Commentary:
Kim and Yura (1996) and Lewis and Zwerneman (1996) confirmed the bearing strength provisions for the bearing case wherein the nominal bearing strength, Rn , is equal to CdtFu and C is equal to 2.4, 3.0 or 2.0 depending upon hole type and/or acceptability of hole ovalization at ultimate load, as indicated in Section J3.10. However, this same research indicated the need for different bearing strength provisions when tearout failure would control. Appropriate equations for bearing strength as a function of clear distance, lc, are therefore provided and this formulation is consistent with that in the RCSC Specification (RCSC, 2014).
Kim, H.J. and Yura, J.A. (1996), “The Effect of End Distance on the Bearing Strength of Bolted Connections,” PMFSEL Report No. 96-1, University of Texas, Austin, TX.
Lewis, B.E. and Zwerneman, F.J. (1996), “Edge Distance, Spacing, and Bearing in Bolted Connections,” Research Report, Department of Civil and Environmental Engineering, Oklahoma State University, Stillwater, OK, July.

## Slide 66: Limit states: Tension connection example
4. Bearing and Tearout at Bolt Holes (J3.10)
When deformation is a design consideration, the design strength is limited to the force at which the hole edge has deformed by a maximum of ¼ in.
When deformation is not a design consideration, larger hole ovalization is permitted as the material attains its maximum bearing strength.
Notes: From AISC 360-16 Commentary:
Frank and Yura (1981) demonstrated that hole elongation greater than 1 /4 in. (6 mm) will generally begin to develop as the bearing force is increased beyond 2.4dtFu, especially if it is combined with high tensile stress on the net section, even though rupture does not occur. For a long-slotted hole with the slot perpendicular to the direction of force, the same is true for a bearing force greater than 2.0dtFu. An upper bound of 3.0dtFu anticipates hole ovalization [deformation greater than 1 /4 in. (6 mm)] at maximum strength. Additionally, to simplify and generalize such bearing strength calculations, the current provisions have been based upon a clear-distance formulation. Provisions prior to 1999 utilized edge distances and bolt spacings measured to hole centerlines with adjustment factors to account for varying hole type and orientation, as well as minimum edge distance requirements.
Frank, K.H. and Yura, J.A. (1981), “An Experimental Study of Bolted Shear Connections,” FHWA/RD-81/148, Federal Highway Administration, Washington, DC, December

## Slide 67: Limit states: Tension connection example
4. Bearing and Tearout at Bolt Holes (J3.10)
When the clear or edge distance is small enough (less than 2d), tearout between the bolt holes or edge of material may occur
lc
d = diameter of bolt

## Slide 68: Limit states: Tension connection example
4. Bearing and Tearout at Bolt Holes (J3.10)
Notes: Equation J3-6c is just the strength associated with 2 shear failures of length equal to the clear distance.
Additional discussion from the J3.10 Commentary:
The effective strength of an individual fastener is the lesser of the fastener shear strength per Section J3.6 and the bearing and tearout strength at the bolt hole per Section J3.10. The strength of a bolt group is a function of strain compatibility and is dependent on the relative stiffnesses of the bolts and connected parts.
For typical connections, such as those shown in the AISC Steel Construction Manual (AISC, 2011) it is acceptable to calculate the shear, bearing and tearout limit states for each bolt in the same connected part and sum the lowest value of the bolt shear or the controlling bearing or tearout limit for each bolt to determine the group strength. The intent is that the separate bearing and tearout equations in this Specification be treated in the same way as the combined equations in the 2010 AISC Specification. This ignores the potential for interaction of these limit states in multiple connected parts, but that impact is small enough in common connection details within the range of the connections shown in Part 10 of the AISC Manual, to allow the benefit of this practical simplification in design. Nonstandard connections may be more sensitive to this interaction; if so, a more exact approach may be necessary.

## Slide 69: Limit states: Tension connection
Bolts
5. Bolt Shear
Shear failure of the bolt along the shear plane (interface).
Strength is proportional to the number of shear planes (interfaces)
shear plane
Notes: Bolt shear is the next limit state. As the load from the angle is transferred to the gusset plate, this causes shear stress along the bolt at a shear plane or shear planes (the interface(s) between the components).

## Slide 70: Limit states: Tension connection Example
Bolts
5. Bolt Shear
shear plane
2 plies of material
(1 shear plane= Single Shear)
3 plies of material
(2 shear planes = Double Shear)
Notes: When determining the shear strength of a fastener, the area, Ab, is multiplied by the number of shear planes.
Depending on the number of plies of material, single or multiple shear planes can exist. These shear planes are the locations where the plies meet one another and transfer forces using the bolt.
1 shear plane is single shear. 2 shear planes is double shear. Double shear has twice the cross-sectional area of a single shear bolt, thus producing twice the shear resistance.

## Slide 71: Limit states: Tension connection Example
Bolts
5. Bolt Shear
Notes: Results of testing showing bolt shear failure. You can see where the shear planes occur.

## Slide 72: Limit states: Tension connection Example
5. Bolt Shear (J3.6)
Notes: Bolt shear is calculated as the ultimate shear stress (see next slide) multiplied by the cross-sectional area of the bolt. Bolt shear strength is influenced by available shear area.
From AISC Design Guide 17:
If the bolt threads are intercepted by one or more shear planes, then less shear area is available than if the threads are not intercepted. The experimental evidence as to what the reduction should be is not clear, however. Tests done in which two shear planes were present support the idea that the shear strength of the bolt is a direct reflection of the available shear area (Kulak et al, 1987). For example, if one shear plane passed through the threads and one passed through the shank, then the best representation was obtained using a total shear area which is the sum of the thread root area plus the bolt shank area. These results support the position that the strength ratio between shear failure through the threads and shear failure through the shank was about 0.70, i.e., the ratio of thread root area to shank area for bolts of the usual structural sizes. Both the RCSC Specification and the AISC LRFD Specification use a higher value, slightly rounded down to 0.80.
For instance, per Table J3.2 : stress on shear plane with threads excluded = 0.563Fu
Stress on shear plane with threads included: 80% of 0.563 Fu = 0.45 Fu
The reduction actually occurs in the area, but is accounted for in the determination of the stress.

## Slide 73: Limit states: Tension connection Example
5. Bolt Shear
Notes: From AISC Design Guide 17:
The response of a single bolt in shear is shown in Fig. 4.2 for both A325 and A490 bolts. The type of test illustrated is done using connecting plates that are loaded in compression. It should be noted that there is little, if any, portion of the response that can be described as linear. Thus, the best measure of the shear capacity of a bolt is its ultimate shear strength. The use of some so-called bolt yield strength is not appropriate. The tests show that the shear strength of a bolt is directly related to its ultimate tensile strength, as would be expected. It is found (Kulak et al, 1987) that the mean value of the ratio of bolt shear strength to bolt tensile strength is 0.62, standard deviation 0.03. An obvious question arising from the bolt shear tests is whether the level of pretension in the bolt affects the results. Test results are clear on this point: the level of pretension present initially in the bolt does not affect the ultimate shear strength of the bolt. This is because the very small elongations used to introduce the pretension are released as the bolt undergoes shearing deformation. Both test results of shear strength for various levels of initial pretension and bolt tension measurements taken during the test support the conclusion that bolt pretensions are essentially zero as the ultimate shear strength of the bolt is reached. This has implications for inspection, among other things. If the capacity of a connection is based on the ultimate shear strength of the bolts, as it is in a so-called bearing-type connection, then inspection for pretension is pointless, even for those cases where the bolts were pretensioned.
G.L. Kulak, J.W. Fisher, and J.A.H. Struik, Guide to Design Criteria for Bolted and Riveted Joints,
Second Edition, John Wiley, New York, 1987.
Reference: AISC Design Guide 17

## Slide 74
(portion of table)
Bolt grades
Notes: The values of nominal shear strength in Table J3.2 were obtained as outlined below. The bolt shear capacity is the nominal stress strength times the area of the bolt. Instead of adjusting the area of the bolt based on with or without threads in the shear plane, the nominal stress is adjusted and the area of the bolt, Ab, does not change.
The factor 0.563 from the table accounts for the effect of a shear/tension ratio of 0.625 and a 0.90 length reduction factor. The factor of 0.45 is 80% of 0.563, which accounts for the reduced area of the threaded portion of the fastener when the threads are not excluded from the shear plane. The initial reduction factor of 0.90 is imposed on connections with lengths up to and including 38 in. (950 mm).

## Slide 75: Limit states: Tension connection Example
5. Bolt Shear
Threads Not Excluded
Threads eXcluded
shear plane
The factor 0.563 accounts for the effect of a shear/tension ratio of 0.625 and a 0.90 length reduction factor.
The factor of 0.45 is 80% of 0.563, which accounts for the reduced area of the threaded portion of the fastener when the threads are not excluded from the shear plane

## Slide 76: Limit states: Tension connection example
Gusset Plate
6. Bearing and Tearout at Bolt Holes
J3-6 equations apply but use gusset plate properties (thickness and material strengths)
6
Notes: The member limit states previously checked for the single angle must also be checked for the gusset plate properties. This includes bearing and tearout at bolt holes. Bearing (shown on left) and tearout (shown on right).

## Slide 77: Limit states: Tension connection example
Gusset Plate
6. Bearing and Tearout at Bolt Holes
7. Block Shear
J4-5 equation applies but consider any possible block shear patterns and use gusset plate properties
6
7
7
Notes: Any possible block shear conditions must be considered. Each possible block shear pattern must be evaluated to determine what controls. Section 7 shows block shear.

## Slide 78: Limit states: Tension connection example
Gusset Plate
6. Bearing / Tearout at Bolt Holes
7. Block Shear
8. Tensile Rupture (use gusset plate properties)
6
8
8
7
7
Notes: Again, must check member limit states for the plate. This includes tensile rupture.

## Slide 79: Limit states: Tension connection example
Gusset Plate
6. Bearing / Tearout at Bolt Holes
7. Block Shear
8. Tensile Rupture
6
7
8
8
9. Tensile Yielding (use gusset plate properties)
9
9
7
Notes: Again, must check member limit states for the plate. This includes tensile yielding.

## Slide 80: Limit states: Tension connection example
Weld
10. Tension Rupture in Weld
Shear failure on the effective throat of the weld.
weld
weld
Notes: Tension rupture (i.e., shear failure on the effective throat) in the weld must be considered.
In this case, because a double-sided weld is shown, both sides would be included in the calculation of the effective area of the weld.

## Slide 81: Limit states: Tension connection example
10. Tension Rupture in Weld
For a linear weld group loaded through the center of gravity:

## Slide 82
(portion of table)

## Slide 83: Limit states: Tension connection example
Effective Area of Fillet Welds (J2.2a)
Leg Size, t
Effective Throat
Failure
Plane
Effective area is effective length multiplied by effective throat
Effective Throat, teff = 0.707t
Effective Area of weld, Awe = teff L
Notes: Rupture of the weld will occur along the failure plane, which is also known as the effective throat. The effective area over which this shear plane occurs is equal to the effective length of the weld multiplied by the effective throat.

## Slide 84: Limit states: Tension connection example
For a 1/16” weld, 1” long
Simplified Weld Strength Equation
Notes: ϕRn = 1.392DL is a quick way of calculating the weld strength of an E70xx weld. D is the number of 1/16th thickness of weld, and L is the effective length of the weld.

## Slide 85: 1- Introduction and Basic Principles
Definitions
Overview of AISC provisions for connections
Connection types
Limit states using tensile connection example
Additional limit states
Notes: Finally, additional limit states beyond those just reviewed that were pertinent to the connection shown, will be reviewed.
Note: if you’re choosing to only spend a few days on connections, you may want to skip over these additional limit states as they are less prevalent.

## Slide 86: ADDITIONAL LIMIT STATES
Additional limit states may also apply in other connection configurations, such as:
Tensile strength of bolts
Bolt subjected to combined shear-tension
Eccentric bolt groups
Eccentric weld groups
Whitmore section
Shear rupture for staggered holes
Prying

## Slide 87: Tensile strength of bolts
Notes: Reference: AISC Design Guide 17

## Slide 88: Tensile strength of bolts
Notes: From AISC Design Guide 17:
The nominal tensile strength of a threaded fastener (Rn ) should be the product of the ultimate tensile strength of the bolt (Fu ) and some cross-sectional area through the threads. The area used is a defined area, the tensile stress area ( Ast ), that is somewhere between the area taken through the thread root and the area of the bolt corresponding to the nominal diameter. Rather than have the designer calculate the area Ast , the LRFD Specification uses an average value of this area for bolts of the usual structural sizes corresponding to the bolt diameter—0.75 times the area corresponding to the nominal bolt diameter. Thus, the nominal tensile strength Fu Ast can be expressed as Fu (0.75Ab ) . The nominal tensile strength is written as Ft Ab. Equating these two expressions, it is seen that Ft = 0.75 Fu . Recall that the ultimate tensile strengths of A325 and A490 bolts are 120 ksi and 150 ksi, respectively. Application of the 0.75 multiplier to change nominal bolt cross-sectional area to tensile stress area gives adjusted stresses ( Ft ) of 90 ksi and 113 ksi for A325 and A490 bolts, respectively.

## Slide 89
(portion of table)

## Slide 90: Bolts subjected to combined shear-tension
Notes: Connections may be loaded and oriented in such a way that bolts are subjected to both shear and tension.

## Slide 91: Bolts subjected to combined shear-tension
(J3.7) The available tensile strength of a bolt subjected to combined tension and shear shall be determined according to the limit states of tension and shear rupture as:
Notes: Note that when the required stress, f, in either shear or tension, is less than or equal to 30% of the corresponding available stress, the effects of combined stress need not be investigated. Also note that Equations J3-3a and J3-3b can be rewritten so as to find a nominal shear stress, F′ nv, as a function of the required tensile stress, ft.

## Slide 92: Bolts subjected to combined shear-tension
Alternative Design Approach
where Fnt = nominal tensile stress, ksi (MPa) Fnv = nominal shear stress, ksi (MPa) ft = required tensile stress, ksi (MPa) fv = required shear stress, ksi (MPa)
Notes: From AISC Commentary, J3.7:
Tests have shown that the strength of bearing fasteners subject to combined shear and tension resulting from externally applied forces can be closely defined by an ellipse (Kulak et al., 1987). The relationship can be expressed as what is shown in the slide.
The elliptical relationship can be replaced, with only minor deviations, by three straight lines as shown on next slide. The sloped portion of the straight-line representation follows.
This latter representation offers the advantage that no modification of either type of stress is required in the presence of fairly large magnitudes of the other type.

## Slide 93
Notes: From AISC Design Guide 17:
Chesson et al. (1965) carried out a series of tests on bolts in this condition, and these test results form the basis for the AISC LRFD rules. Two grades of fastener were tested: A325 bolts and A354 grade BD bolts. The latter have mechanical properties equivalent to A490 bolts. The test program showed that the only variable other than bolt grade that affected the results was bolt length. This was expected: as bolt length increases bending takes place and the bolt shear strength increases slightly. (This is the consequence of the fact that the shear planes through a curved bolt are slightly larger than if the bolt were straight.)
An elliptical interaction curve was fitted to the test results. The shear stress is calculated on the applicable area, the shank or through the threads, and the tensile stress is calculated on the tensile stress area. The researchers also suggested a three-straight line approximation to the results, and this is the model used in the LRFD rules.
Chesson, Eugene, Jr., Munse, William H., and Faustino, Norberto R., "High-Strength Bolts Subjected to Tension and Shear," Journal of the Structural Division, ASCE, Vol. 91, ST5, October,
1965.

## Slide 94: Bolts subjected to combined shear-tension
The elliptical relationship can be replaced, with only minor deviations, by three straight lines as shown in Figure C-J3.2. The sloped portion of the straight-line representation follows:

## Slide 95: Eccentrically loaded bolt groups
The tensile connection example presented earlier in this module contained bolts that were concentrically loaded.
Connections may result in eccentrically loaded bolts. This eccentricity can be accounted for in the design using:
  Elastic Analysis
  Instantaneous Center of Rotation

## Slide 96: Eccentrically loaded bolt groups
Centroid of bolt group
Direct Shear
Moment Shear
Mu=e
Elastic Analysis
Bolt shear is evenly distributed among each bolt
Assumed rotation about the center of gravity of bolt group
e
Pu
Pu

## Slide 97: Eccentrically loaded bolt groups
Instantaneous Center (approach used in AISC tables)
Accounts for translation and rotation of the bolt group
Centroid of bolt group, CG
Instantaneous Center, IC
Pu
e

## Slide 98: Eccentrically loaded bolt groups
Instantaneous Center (approach used in AISC tables)
The location of the instantaneous center (IC) affects the demand on the bolts. Need to determine location of IC
e
IC ?
α
α
xo
yo

## Slide 99: Eccentrically loaded bolt groups
Instantaneous Center (approach used in AISC tables)
IC
Ri are the resistances (forces) in each bolt
Ri is perpendicular to di and proportional to di
di is measured from each bolt to IC
di
Ri
(Figure 7-3)

## Slide 100: Eccentrically loaded bolt groups
Instantaneous Center (approach used in AISC tables)
(Figure 7-3)

## Slide 101: Eccentrically loaded bolt groups
Instantaneous Center (approach used in AISC tables)
IC
di
Ri
α
yo
xo
With the correct IC location, the system will be in equilibrium: balance of external force, P, with the bolt resistance forces.
e
α
P
Notes: From Part 7 of AISC Steel Construction Manual:
The shear strength of the bolt most remote from the IC can be determined by applying a maximum deformation, Δmax to that bolt. The load-deformation relationship is based upon data obtained experimentally (for ¾” diam. ASTM F3125 Grade A325 bolts in double shear, where Rult=74 kips and Δmax =0.34 in).
The nominal shear strengths of the other bolts in the joint can be determined by applying a deformation Δ that varies linearly with distance from the IC. The nominal shear strength of the bolt group is, then, the sum of the individual strengths of all bolts.
The individual resistance of each bolt is assumed to act on a line perpendicular to a ray passing through the IC and the centroid of that bolt. If the correct location of the IC has been selected, the three equations of in-plane state equilibrium will be satisfied. For further information, see Crawford and Kulak (1971).
Crawford, S.F. and Kulak, G.L. (1971) “Eccentrically Loaded Bolted Connections,” Journal of the Structural Division, ASCE, Vol. 97, No. ST3, pp. 765-784.

## Slide 102: Eccentrically loaded bolt groups
Instantaneous Center (approach used in AISC tables)
IC
di
Ri
α
yo
xo
e
α
P
xi | yi | di | Δi | Ri | Rixi/di | Ridj
Only furthest away bolt can reach Δmax
IC location can be determined by iterating
Sum the individual strengths of all bolts to achieve system equilibrium
Notes: This procedure of solving the instantaneous center is iterative. It can be done using the solver in Excel.

## Slide 103: Eccentric bolt groups – Design Aids
Table 7-6 through 7-13– Coefficients C for Eccentrically Loaded Bolt Groups
Tables employ instantaneous center of rotation method for bolt patterns and eccentric conditions
Notes: Table 7-6 (next slide) is a design table in the AISC Steel Construction Manual. It calculates a “C” value to multiply by the strength of a bolt in order to determine the available strength of the bolt group. The instantaneous center approach was used to generate these values.

## Slide 104
Tables include: Inclined loads at 0o, 15o, 30o, 45o, 60o and 75o
Bolt spacing varies: 3” and 6”
Number of bolts in row: 2-12
Considers multiple rows with different gages
Eccentricity varies: 2” – 36”

## Slide 105: Eccentrically loaded wELD groups
The tensile connection example from Module 1 contained welds that were concentrically loaded.
Connections may result in eccentrically loaded welds, which can be designed using the methods below.
Like eccentric bolt groups, two methods exist:
Elastic Method
Instantaneous Center of Rotation Method

## Slide 106: Eccentrically loaded wELD groups
Length of weld
Polar moment of inertia
Distance from weld center
Mu=Pue
Elastic Analysis
Notes: From Part 8 of AISC Steel Construction Manual:
Eccentricity in the plane of the faying surface produces additional shear. The welds must be designed to resist the combined effect of the direct shear, Pu, and the additional shear from the induced moment, PuE. Two methods of analysis for this type of eccentricity are the instantaneous center of rotation method and the elastic method. The instantaneous center of rotation method is more accurate but generally requires the use of tabulated values or an iterative solution. The elastic method (shown above) is simplified, but may be excessively conservative because it neglects the ductility of the weld group and the potential load increase.

## Slide 107: Eccentrically loaded wELD groups
Instantaneous Center of Rotation Method
Similar iterative approach used with bolts applied to weld lines based on the load-deformation relationship for a unit length segment of weld
See Part 8 in AISC Manual for more details.
Notes: From Part 8 of AISC Steel Construction Manual:
Eccentricity produces both a rotation and a translation of one connection element with respect to the other. The combined effect of this rotation and translation is equivalent to the rotation about a point defined as the instantaneous center of rotation (IC) as illustrated in the figure. The location of the IC depends upon the geometry of the weld group as well as the direction of application of the load.
Fig 8-5 in the manual shows fillet weld strength vs deformation relationship.
Equation 8-3 gives the nominal stress of a weld element based on presumed ultimate deformation

## Slide 108: Eccentric Weld groups – Design Aids
Table 8-4 through 8-11– Coefficients C for Eccentrically Loaded Weld Groups
Tables employ instantaneous center of rotation method for weld patterns and eccentric conditions
Notes: Like the design tables for eccentric bolt groups, there are also design tables in the AISC Steel Construction Manual for eccentric weld groups. These tables calculate a “C” value to determine the available strength of the weld group. The instantaneous center of rotation approach was used to generate these values.

## Slide 109
Tables include: Inclined loads at 0o, 15o, 30o, 45o, 60o and 75o
a = ex/l
Considers different geometries (vertical/ horizontal lines, rectangles, C-shapes, L-shapes)
k = weld spacing/l

## Slide 110: Whitmore section
Theoretical effective cross-sectional area based on a 30 degree spread-out for gross and net sections (Part 9 of Steel Manual)
Critical section
Notes: A Whitmore section identifies a theoretically effective cross-sectional area at the end of a connection resisting tension or compression, such as that from a brace-to-gusset-plate connection or similar fitting. The effective length for the Whitmore section Lw is determined by using a spread-out angle of 30° along both sides of the connection, beginning at the start of the connection. It is applicable to both welded and bolted connections.
It is a simple way to determine how force from a brace spreads through a gusset plate. It’s used to make checks of gusset plate yielding and buckling possible.
Reference: How to use the Whitmore method for tension and compression strength checks – AISC Steelwise: https://www.aisc.org/globalassets/modern-steel/steelwise/072011_july11_steelwise_web.pdf

## Slide 111: Whitmore section
Notes: Here you can see examples of the zones within the gusset that represent the Whitmore section based on the geometry of the connection and the loading.
Reference: How to use the Whitmore method for tension and compression strength checks – AISC Steelwise: https://www.aisc.org/globalassets/modern-steel/steelwise/072011_july11_steelwise_web.pdf

## Slide 112: Whitmore section
Gusset plate that has failed in tension rupture after significant tension yielding at the Whitmore section
The predicted strength was in good agreement with the measured failure load
Murray, VA Tech
Notes: Reference: How to use the Whitmore method for tension and compression strength checks – AISC Steelwise: https://www.aisc.org/globalassets/modern-steel/steelwise/072011_july11_steelwise_web.pdf

## Slide 113: Shear Rupture for staggered holes
s
g
g
Net Area Determination (Section B4.3b)
Net area, An = gross area minus area of holes + the adjustment for stagger
= Ag – Ah + stagger
Stagger = s2 /4g
Notes: When bolt holes are staggered, you must consider shear rupture along potential diagonal / zigzag planes.
From AISC 360-16, Section B4:
For a chain of holes extending across a part in any diagonal or zigzag line, the net width of the part shall be obtained by deducting from the gross width the sum of the diameters or slot dimensions as provided in this section, of all holes in the chain, and adding, for each gage space in the chain, the quantity s2 /4g,
where g = transverse center-to-center spacing (gage) between fastener gage lines, in. (mm) s = longitudinal center-to-center spacing (pitch) of any two consecutive holes, in. (mm)

## Slide 114: Shear Rupture for staggered holes
2”
3”
3”
Example for ½” plate with ¾” diam. bolts with standard holes
Ag = 9 in. x ½” = 4.5 in2
Ah = 3(dh+ ”)(½”)
= 1 in2
Stagger Area = (s2 /4g ) (½”)
= 2 [(2”)2/(4x3”)] (½”)
= 0.33 in2
1.5”
1.5”
Notes: This is an example for how to calculate the stagger area to be used to determine the shear rupture strength of the connection. The net area to use in calculating the shear rupture strength can be determined from the following calculation: Ag – Ah + stagger (gross area minus the area of the holes plus the stagger area).

## Slide 115: Shear Rupture for staggered holes
2”
3”
3”
An = Ag - ∑Ah + ∑stagger
= 4.5 in2 - 1 in2 +0.33 in2
= 3.65 in2
1.5”
1.5”

## Slide 116: Shear Rupture for staggered holes
Notes: Results from experimental testing (photo courtesy of Jason McCormick at University of Michigan).

## Slide 117: Prying
Phenomenon (in bolted construction only, and only in connections with tensile bolt forces) where the deformation of a connecting element under a tensile force increases the tensile force in the bolt above that due to direct tensile force alone.
Notes: Prying is a phenomenon (in bolted construction only, and only in connections with tensile bolt forces) where the deformation of a connecting element under a tensile force increases the tensile force in the bolt above that due to the direct tensile force alone.
Proper design for prying action includes the selection of bolt diameter and fitting thickness, t, such that there is sufficient stiffness and strength in the connecting element and strength in the bolt. The design basis has been changed to calculate strength in terms of Fu, which provides better correlation with available test data than previous design methods. For the development of prying action equations, see Thornton (1992) and Swanson (2002) cited in the Steel Manual.
Citation: https://www.aisc.org/globalassets/product-files-not-searched/engineering-journal/1985/22_2_067.pdf

## Slide 118: Prying
Notes: From the AISC Steel Construction Manual, Part 9:
The dimensions b and b’ in Figure 9-4 are measured from the face of the tee stem or the center of the angle leg. These values are valid for tees and for angles if the load, 2Tu is delivered symmetrically and the angle shown represents one of a pair of back-to-back angles. When the angles are not back-to-back and connected to a relatively flexible support, the effective eccentricity may be increased and a distance measured to the heel of the angle or possibly somewhat larger might be warranted. It is common to assume there is no moment transfer between the flange and the element to which it is attached; that is, all the moment required for equilibrium of the flange is assumed to be taken at the bolt line. This discussion is not intended to be applied to asymmetrical conditions. When the load is delivered asymmetrically, an even greater moment will result. For instance, if the angle is attached to only one flange of a wide-flange member used as a hanger and the hanger is not restrained from rotating about the bolt line, then the eccentricity would be measured from the centerline of the hanger or to the point of application of the load.
For the hanger connection shown, the deformation of the connected tee flange or angle leg is assumed to be in double curvature if prying forces exist. Tr is the required tension force per bolt using LRFD load combinations and qr is the corresponding prying force.

## Slide 119: Prying
The required thickness to eliminate prying action, tnp:
Notes: This equation calculates the required thickness to eliminate prying action. If the connecting element has a thickness at least as large as the value calculated in this equation, prying action will not occur and no further check of prying action is required.

## Slide 120: Prying
When required thickness is reasonable, no further check of prying action is necessary.
The thickness required to ensure an acceptable combination of fitting strength and stiffness and bolt strength:
Notes: This equation is used if you are designing for the actual effects of prying action (i.e. will get a lesser required thickness that Equation 9-17).

## Slide 121: Prying

## Slide 122: Prying